## Slide 1: Early Experiences with Energy-Aware (EAS) Scheduling
Presentation Date

## Slide 2: Agenda
    Project Motivation
    Overview
    Efforts To date
    Results
    Ongoing Efforts
    Summary

## Slide 3: Project Motivation
With the average HPCMP HPC System Utilization in the 80% range, opportunities exist to power off idle compute nodes, reducing energy costs for the idle nodes and associated cooling.
Scheduling of reservations, system maintenance events, and scheduling of large node count jobs all create opportunities to power off idle nodes.
Idle nodes consume approximately 50% of the power of an active node.

## Slide 4: Overview
Project initiated via HPCMP Energy Efficiency Initiatives 8/11.
Motivation: Explore the feasibility of powering off resources that are idle to save energy.
  There are commercial implementations on cyclic workloads that have proven successful, but is it feasible for large non-cyclic HPC workloads?
Theory: Typically HPCMP systems run ~ 80% utilization. If we can power off 10% of system’s nodes there would be significant energy and monetary savings to the program. Annual HPCMP kWh saving by x% of systems for y hours/day.
Architecture | 10% 12h/D | 15% 12h/D | 10% 24h/D | 15% 24h/D
XE6 | 224012 | 336018 | 448024 | 672036
Altix | 263725 | 395588 | 527450 | 791175
Subtotal | 487737 | 731606 | 975474 | 1463211
Site (1.8 PUE) | 390190 | 585284 | 780379 | 1170569
Total | 877927 | 1316890 | 1755853 | 2633780

## Slide 5: Overview (continued)
Issues considered
  No reduction in service delivery or increased expansion factors
  Software/system viability: Architecture considerations: e.g. CRAY XT5 architecture will not recover from off node
  No significant performance degradation for jobs
  Idle nodes use 50%-60% of active nodes
  System reliability affects
  Cooling requirement reductions

## Slide 6: Efforts To date
Altair base code for commercial application significantly adapted to the scale of HPC systems/job mix, and non-cyclic job model.
Standardized system interfaces created for system control.
Code updated to be backfilled aware.
Significant development/testing on ARL Test & Development Systems (TDS)
  passive mode
  live mode
Network Affects test on Tana (CRAY XE6, 256 cores)

## Slide 7: Efforts To date (continued)
Production on Army Research Laboratory DoD Supercomputing Resource Center (ARL DSRC) systems
  Harold (SGI Altix ICE Quad Core Xeon Cluster 10,752 cores)
  TOW (SGI Altix ICE Quad Core Xeon Cluster 6,656 cores)
  ICECUBE (SGI Altix ICE Quad Core Xeon Cluster TDS, 96 cores)
  MJM (Linux Networx Evolocity II Xeon Cluster, 3.248 cores)
    Development applicable to Mana: US and other IB clusters
  Abutil (Appro Xtreme-X Series Cluster 1,824 cores)
  Cabutil (Appro Xtreme-X Series Cluster 1,008 cores)
Production on Maui High Performance Computing Center (MHPCC) system
  Mana (Dell Quad Core Xeon Cluster (9,216 cores)
    Transitioned slowly to “live mode” starting 25 Apr 12
  Muutil (Appro Quad Core Xeon Cluster
    EAS/PBSPro 11.2 installed. Ran in passive mode for 2 months. Waiting for approval.

## Slide 8: Harold (SGI Altix ICE 10,752 cores) Results
Chart: HAROLD Number of Nodes Powered-Off

## Slide 9: Harold Results (continued)
Moved reservation nodes from racks 17-21 to racks 1-5.
  Improved backfill jobs and freed up nodes for longer running jobs
Scheduled PM on 5/27 shows nodes powered down as no pending jobs could complete prior to PM reservation.
Emergency PM on 6/12 shows nodes powered down due to system inactivity.

## Slide 10: Harold Results (continued)
Harold EAS Savings Harold Utilization
  Apr 11,498 hrs ( 1,690 kWh) - 95.5% for Apr (7,396.061 hrs)
  May 31,604 hrs ( 4,645 kWh) - 89.9% for May (7,194,403 hrs)
  Jun 30,102 hrs ( 4,424 kWh)
  Jul 1,273 hrs ( 187 kWh)
  Aug 18,385 hrs ( 3,280 kWh)
  Limited Opportunity to save energy on Harold at its current level of utilization.
Estimated Yearly Savings is $6,000

## Slide 11: Harold Lifecycle Utilization
Chart: Month
| 40057 | 40087 | 40118 | 40148 | 40179 | 40210 | 40238 | 40269 | 40299 | 40330 | 40360 | 40391 | 40422 | 40452 | 40483 | 40513 | 40544 | 40575 | 40603 | 40634 | 40664 | 40695 | 40725 | 40756 | 40787 | 40817 | 40848 | 40878 | 40909 | 40940 | 40969 | 41000 | 41030
 | 72 | 63 | 39 | 23 | 47 | 58 | 67 | 71 | 58 | 73 | 75 | 81 | 81 | 78 | 52 | 70 | 81 | 90 | 86 | 80 | 86 | 73 | 56 | 71 | 83 | 79 | 77 | 78 | 92 | 81 | 87 | 97 | 100
Vendor ELT
CAP
Start of Production
(6 months to exceed 80%)
OS Upgrade
Harold took 7 months from start of production to reach 80% utilization.
$200K of power cost expended over life cycle for idle nodes.

## Slide 12: TOW (SGI Altix ICE 6,656 cores) Results
Chart: TOW Number of Nodes Powered-Off

## Slide 13: TOW Results (continued)
Lustre issues with too many nodes powering-on
EAS disabled while node startup issues addressed. Lustre upgrade and tuning/EAS resumed on a limited set of nodes.
Low EAS usage since 5/11 with increased workload/130 node dedicated project
TOW EAS savings TOW Utilization
  Apr 15,555 hrs ( 2,286 kWh ) - 59.9% for Apr (2,872,756)
  May 1,333 hrs ( 195 kWh ) - 73.5% for May (3,617,621)
  Jun 6,335 hrs ( 931 kWh )
  Jul 4,023 hrs ( 591 kWh)
  Aug 7,337 hrs (1,078 kWh)

## Slide 14: Abutil (Appro Xtreme Cluster 1,408 cores) Results
Chart: ABUTIL Number of Nodes Powered-Off

## Slide 15: Abutil Results (continued)
EAS Configured on Abutil in February
EAS was disabled for short period for user code testing
Abutil EAS Savings Abutil Utilization
  Apr 29,267 hrs ( 11,024 kWh ) - 3.9% for Apr ( 49,924 hrs )
  May 38,044 hrs ( 13,934 kWh ) - 3.6% for May ( 47,803 hrs )
  Jun 37,007 hrs ( 13,544 kWh )
  Jul 21,602 hrs ( 7,819 kWh )
  Aug 21,195 hrs ( 7.826 kWh )
  July timeframe implemented keep-alive feature and increased the powered-on nodes.
Daily Average of 53 of 88 Nodes Powered-off
Estimated Yearly Savings is approx $22k

## Slide 16: ARL Cabutil Results
Chart: CABUTIL Number of Nodes Powered-Off

## Slide 17: ARL Cabutil (continued)
EAS Configured on Cabutil in March
EAS Disabled for a Short Period to Test User Code
Cabutil EAS Savings Cabutil Utilization
  Apr 18,900 hrs ( 6,128 kWh ) - 0.8% for Apr ( 5,541 hrs)
  May 18,701 hrs ( 6,063 kWh ) - 7.9% for May ( 58,163 hrs)
  Jun 20,840 hrs ( 7,383 kWh )
  Jul 19,530 hrs ( 6,798 kWh )
  Aug 10,306 hrs ( 3,390 kWh)
Estimated Yearly Savings is approx $11k
Daily Average of 37 of 44 nodes powered-off

## Slide 18: MHPCC Mana Results
Chart: MANA Number of Nodes Powered-Off

## Slide 19: MHPCC Mana Results
Chart: MANA Number of Nodes Powered-Off

## Slide 20: MHPCC Mana Results (continued)
Chart: MANA Hours Powered Off & Cost Savings
| 41000 | 41030 | 41061 | 41092 | 41123
MANA hours powered off for the month | 495022 | 247144 | 203243 | 261925 | 212803
MANA estimated Dollar savings at site | 28216 | 14086 | 11584 | 19325 | 12129

## Slide 21: MHPCC Mana Results (continued)
EAS Configured on Mana in March
Mana Monthly Savings:
  Apr: 495,022 hrs ( 74,253 kWh ) - virtual savings
  May 247,144 hrs ( 37,071 kWh ) - about 50% of the system was under EAS control
  Jun 203,243 hrs ( 30,486 kWh ) - less than 50% was under EAS control
  Jul 261,925 hrs ( 39,273 kWh )
  Aug 212,803 hrs ( 31,920 kWh )
Mana Estimated Yearly Savings approx $160k

## Slide 22: Ongoing Efforts
Upgrade to PBSPro 11.3
  Currently testing at ARL
Utility Server
  Implement EAS on AFRL, ERDC and NAVY DSRC Utility Servers
Implement EAS on TI-12 systems across the HPCMP

## Slide 23: Summary
EAS found to be feasible on many architectures.
EAS needs to be more tightly integrated with scheduler.
EAS appears to be compatible with the IBM iDataPlex TI-12 systems.
HPC Vendor resistance has been encountered but EAS node shutdown/startup provides an opportunity to perform proactive hardware checks, improving long term reliability.

## Slide 24: Summary (continued)
Measured power savings are encouraging.
Thanks to all!
  ARL (Project Sponsorship & Executive Agent).
  Lockheed Martin (LM) (Architectural Implementation, Algorithm Development, Performance/Feasibility Evaluation).
  Altair (Algorithm Development, Scheduler Interface)
  Instrumental (Architectural Implementation, HPCMP Coordination)
  Air Force Research Laboratory Maui High Performance Computing Center (MHPCC)
  ORS: XE6 evaluation.
  SGI (System monitoring, Architectural Implementation).
  APPRO: Support for EAS on HPCMP Utility Servers

## Slide 25: Questions
Questions?